## Slide 1: Leak Detection for Liquid-Cooled PCBs in Datacenter Systems
Best practices: detection reliability, cost, board integration
Igor Gurevich — Sept 2026

## Slide 2: Why Leak Detection Matters
Direct-to-chip liquid cooling is mainstream for high-TDP boards
One undetected leak = board loss, rack downtime, cascading damage
Goals: fast detection, low false positives, low BOM cost, BMC-actionable

## Slide 3: Method 1: Rope/Cable Sensors
Cable routed under cold plates, tubing, chassis low points
Detects liquid anywhere along length (R or C change)
+ Wide coverage, flexible, reusable
– Condensation false positives, routing complexity, moderate cost
Best for: system/chassis-level protection

## Slide 4: Method 2: Interdigitated PCB Traces
Exposed comb/grid copper at high-risk locations; liquid bridges gap
+ Near-zero BOM cost, standard PCB process, pinpoint, fast
– Limited coverage, flux contamination risk, on-board only
Best for: cold plate ports, QD fittings, under connectors

## Slide 5: Method 3: Point (Spot) Sensors
Packaged discrete sensors at key locations
+ High sensitivity, simple readout, off-the-shelf (Honeywell, Sensata)
– Tiny coverage area; many units needed for distributed protection
Best for: critical single-point risks

## Slide 6: Method 4: Capacitive Sensors
Detect liquid via capacitance change on pads
+ Rejects condensation, works through conformal coating
– More complex electronics, higher cost
Best for: environments intolerant of false positives

## Slide 7: Comparison Matrix
Rope/Cable: High reliability | Mod cost | Large coverage
Interdigitated: Med-High | Low cost | Localized
Point Sensors: Medium | Low cost | Localized
Capacitive: High | Mod-High cost | Localized/Medium

## Slide 8: Best Practices
Redundancy: wide-area rope + point-of-risk traces
Placement: under ports, along coolant lines, gravity low points
Validate sensors against coolant chemistry (PG25 vs dielectric)
BMC integration: debounce logic → alert, pump stop, valve isolation

## Slide 9: Recommended Architecture
PCB comb traces at cold plate fittings & QDs (~free in BOM)
Rope sensor along manifold/tubing path & chassis low points
Signals → BMC with condensation-rejection logic
Confirmed leak → automated flow isolation + alert
Industry practice: Dell/HPE/Lenovo hybrid approach

## Slide 10: References
Schneider Electric — Liquid Leak Detection in Datacenters
Honeywell — Liquid Leak Detection Sensors
ASUS — Liquid Cooling Solutions for Servers whitepaper